## SMDB-1
PROJECT : JBH - TALISE GYM |  |  |  |  | DETAILS OF CONNECTED LOAD / MAX. DEMAND | [7 empty] | LOCATION: 1ST FLOOR ELECT. ROOM GRID 54
SMDB REF : SMDB-1
FED FROM : MDB-2
SR. | CIRCUIT | SP/ | RATING-AMPS |  | FAULT | PVC/XLPE |  | ECC | CONNECTED LOAD-KW |  |  |  | KWH METER |  |  |  | REMARKS
NO. | FEEDER | TP | ISO | ACB | DUTY | SWA/PVC | 2/3/4C | SIZE-1C | R-PHASE | Y-PHASE | B-PHASE | TOTAL | 1 Ph | 3 Ph | 3 Ph | C.T
| DB NO. |  |  | MCCB | KA |  | mm2 | mm2 | KW | KW | KW | KW | (1) | (2) | (3) | 4
| INCOMER | TP | 630 |  | 35 | XLPE/SWA/PVC | 2-4Cx240 | 2-1Cx120 | 130.02 | 127.16 | 119.59 | 376.77 |  |  |  | 1
| OUTGOING: | [11 empty] | REMARKS
1 | DB-1-N2 | TP |  | 63 | 32 | XLPE/SWA/PVC | 4Cx35 | 1Cx16 | 9.9 | 8.05 | 6.7 | 24.65 | NEW
2 | DB-1-N4 | TP |  | 63 | 32 | XLPE/SWA/PVC | 4Cx25 | 1Cx16 | 10.95 | 10.42 | 11.07 | 32.44
3 | DB-1-N1 | TP |  | 63 | 32 |  | 2CX25 | 1Cx16 | 11.23 | 6.33 | 8.75 | 26.31
4 | DB-1-27.00 | TP |  | 63 | 32 | XLPE/SWA/PVC | 4Cx25 | 1Cx16 | 5.6 | 3 | 3.2 | 11.8
5 | DB-1-K1 | TP |  | 100 | 32 | XLPE/SWA/PVC | 4Cx70 | 1Cx35 | 8.81 | 8.06 | 9.56 | 26.43
6 | DB-1-23 | TP |  | 63 | 32 | XLPE/SWA/PVC | 4Cx25 | 1Cx16 | 3.73 | 4.31 | 3.97 | 12.01
7 | DB-1-39.00 | SP |  | 63 | 32 |  | 2CX25 | 1Cx16 | 0 |  |  | 0 | CANCELLED FROM PHASE 3
8 | DB-1-40.00 | SP |  | 63 | 32 |  | 2CX25 | 1Cx16 |  | 0 |  | 0 | CANCELLED FROM PHASE 3
9 | DB-1-41.00 | SP |  | 63 | 32 |  | 2CX25 | 1Cx16 |  |  | 0.25 | 0.25 | AS PER AS-BUILT LOAD SCHED.
10 | SMDB-DB-1-N3 | TP |  | 250 | 32 | XLPE/SWA/PVC | 4Cx240 | 1Cx120 | 27.9 | 34.21 | 24.39 | 86.5 | REFER TO TALISE GYM
11 | DB-1-32.00 | SP |  | 63 | 32 |  | 2CX25 | 1Cx16 | 4.5 |  |  | 4.5
12 | DB-1-35.00 | SP |  | 63 | 32 |  | 2CX25 | 1Cx16 |  | 4.5 |  | 4.5
13 | DB-1-38.00 | SP |  | 63 | 32 |  | 2CX25 | 1Cx16 |  |  | 4.5 | 4.5
14 | DB-1-36.00 | SP |  | 63 | 32 |  | 2CX25 | 1Cx16 | 4.5 |  |  | 4.5
15 | DB-1-37.00 | SP |  | 63 | 32 |  | 2CX25 | 1Cx16 |  | 4.5 |  | 4.5
16 | DB-1-35.01 | SP |  | 63 | 32 |  | 2CX25 | 1Cx16 |  |  | 4.5 | 4.5
17 | DB-1-RL | TP |  | 63 | 32 | XLPE/SWA/PVC | 4Cx25 | 1Cx16 | 6.3 | 4.5 | 6.3 | 17.1
18 | SPARE | SP |  | 63 | 32 | [6 empty] | 0
19 | DB-1-25.00 | SP |  | 63 | 32 |  | 2CX25 | 1CX16 |  | 0.25 |  | 0.25
20 | DB-1-24.02 | SP |  | 63 | 32 |  | 2CX25 | 1CX16 |  |  | 4.2 | 4.2
21 | CB-1-N4 | SP |  | 25 | 32 |  | 2CX10 | 1CX10 | 1.1 |  |  | 1.1
22 | SPARE | SP | [9 empty] | 0
23 | SPARE | SP | [9 empty] | 0
24 | SPARE | TP | [9 empty] | 0
25 | DB-1-SPA-1 | TP |  | 100 | 32 | XLPE/SWA/PVC | 4CX35 | 1CX16 | 15.786 | 15.7875 | 13.417 | 44.9905 | REPLACE DB-1-42.00
26 | CB-1-N1 | SP |  | 25 | 32 |  | 2CX6 | 1CX6 | 1.16 |  |  | 1.16
27 | CB-1-N2 | SP |  | 25 | 32 |  | 2CX10 | 1CX10 |  | 0.18 |  | 0.18
28 | CB-1-N3 | SP |  | 25 | 32 | XLPE/SWA/PVC | 2CX10 | 1CX10 |  |  | 1.03 | 1.03
29 | DB-1-SPA-2 | TP |  | 160 | 32 | XLPE/SWA/PVC | 4CX70 | 1CX35 | 22.1593 | 26.2733 | 21.1983 | 69.631 | REPLACE DN-1-K2
30 | DB-1-N5 | TP |  | 63 | 32 | XLPE/SWA/PVC | 4CX25 | 1CX16 | 5.67 | 5.67 | 5.52 | 16.86
MDB CONNECTED TO : DEWA LV /DB / TRANSF. |  |  |  |  | TOTAL CONNECTED LOAD PER PHASE | [11 empty] | TOTAL
[8 empty] | TOTAL | 139.2953 | 136.0408 | 128.5553 | 403.8915 |  |  |  |  | 403.8915
| DEMAND FACTOR |  | 0.85 |  |  | 343.3078 | TOTAL CONNECTED LOAD |  | 403.8915 | KW
| Type of Meter (Rating of Incomer) : | [5 empty] | (1) UPTO 60A |  |  | (4) LV CT..…-..../....-..…A |  |  |  | (5)HV CT……-…./…-…A
[6 empty] | (3 PHASE) | (1 PHASE)

## DB-1-N2
Project : | JBH - TALISE GYM | [5 empty] | LOAD DISTRIBUTION SCHEDULE
DB No: DB-1-N2 | [6 empty] | (3-PHASE)
Fed from: SMDB/1
NOTE: | [24 empty] | Location of DB : |  | 1ST FLOOR, NORTHWING
Rating of Incomer | Ratg of ELCB | SL. NO. | CIR. No. | MCB Rtg in (A) | CCT wire size mmsq | RCC wire size mmsq | Room / Area | Connected Load / Points | [16 empty] | Watts Each | Load Per Phase - Watts |  |  | Remarks
[13 empty] | LTG | LTG | LTG | 13A | 13A | 15A | WH | HD | FCU | SPUR | ISOL | TOTAL
[13 empty] | 1 | 2 | 3 | SO | TSO | SO | [7 empty] | R | Y | B
[8 empty] | LTG | HO OD | EX. FAN | SH. S/O | 13A SSO |  |  |  | 200 | 400
63A TPN ISOLATOR | 63A 100mA 4P | 1 | R1 | 10 | 2.5 | 2.5 | F&B / DIV MANAGER OFFICE LIGHTING | [5 empty] | 8 | [11 empty] | 100 | 800
|  | 2 | Y1 | 10 | 2.5 | 2.5 | SECRETARY AREA LIGHTING | [5 empty] | 8 | [11 empty] | 100 |  | 800
|  | 3 | B1 | 10 | 2.5 | 2.5 | COPY RM/CHIEF ENGR/STORE LIGHTING | [5 empty] | 5 | [11 empty] | 100 |  |  | 500
|  | 4 | R2 | 10 | 2.5 | 2.5 | DIR OF PERSONNEL OFFICE LIGHTING | [5 empty] | 7 | [11 empty] | 100 | 700
|  | 5 | Y2 | 10 |  |  | SPARE | [19 empty] | 0
|  | 6 | B2 | 10 |  |  | SPARE | [20 empty] | 0
| 63A 100mA 4P | 7 | R3 | 10 |  |  | SPARE | [18 empty] | 0
|  | 8 | Y3 | 10 |  |  | SPARE | [19 empty] | 0
|  | 9 | B3 | 10 |  |  | SPARE | [20 empty] | 0
|  | 10 | R4 | 10 |  |  | SPARE | [18 empty] | 0
|  | 11 | Y4 | 10 | 2.5 | 2.5 | LINEN ROOM LIGHTING | [5 empty] | 5 | [11 empty] | 50 |  | 250
|  | 12 | B4 | 10 |  |  | SPARE | [20 empty] | 0
| 63A 30mA 4P | 13 | R5 | 20 | 4 | 4 | FEMALE RELAXATION ROOM | [8 empty] | 1 | 2 | [8 empty] | 1000 |  |  | RING
|  | 14 | Y5 | 10 |  |  | SPARE | [19 empty] | 0
|  | 15 | B5 | 10 |  |  | SPARE | [20 empty] | 0
|  | 16 | R6 | 10 |  |  | SPARE | [18 empty] | 0
|  | 17 | Y6 | 10 |  |  | SPARE | [19 empty] | 0
|  | 18 | B6 | 10 |  |  | SPARE | [20 empty] | 0
| 63A 30mA 4P | 19 | R7 | 32 | 4 | 4 | F&B / DIV MNAGER 13A RING | [9 empty] | 4 | [8 empty] | 1600
|  | 20 | Y7 | 32 | 4 | 4 | SECRETARY AREA 13A RING | [9 empty] | 6 | [9 empty] | 2400
|  | 21 | B7 | 32 | 4 | 4 | COPY RM/CHIEF ENGR/STORE 13A RING | [9 empty] | 7 | [10 empty] | 2800
|  | 22 | R8 | 32 | 4 | 4 | DIR OF PERSONNEL OFICE 13A RING | [9 empty] | 4 | [8 empty] | 1600
|  | 23 | Y8 | 32 |  |  | SPARE | [19 empty] | 0
|  | 24 | B8 | 32 |  |  | SPARE | [20 empty] | 0
| 63A 30mA 4P | 25 | R9 | 32 | 4 | 4 | FEMALE TREATMENT ROOM 1 | [9 empty] | 4 | [8 empty] | 1600 |  |  | RING
|  | 26 | Y9 | 32 | 4 | 4 | FEMALE TREATMENT ROOM 2 | [9 empty] | 4 | [9 empty] | 1600 |  | RING
|  | 27 | B9 | 32 | 4 | 4 | FEMALE TREATMENT ROOM 3 | [9 empty] | 4 | [10 empty] | 1600 | RING
|  | 28 | R10 | 32 | 4 | 4 | FEMALE TREATMENT ROOM 4 | [9 empty] | 4 | [8 empty] | 1600 |  |  | RING
|  | 29 | Y10 | 32 | 4 | 4 | FEMALE TREATMENT ROOM 5 | [9 empty] | 4 | [9 empty] | 1600 |  | RING
|  | 30 | B10 | 32 | 4 | 4 | FEMALE PREP | [8 empty] | 1 | 2 | [10 empty] | 1000 | RING
| 63A 100mA 4P | 31 | R11 | 20 | 4 | 4 | F@B/DIV MANAGER/DIR PER FCU | [13 empty] | 3 |  |  |  | 200 | 600
|  | 32 | Y11 | 20 | 4 | 4 | SECRETARY AREA FCU | [13 empty] | 2 |  |  |  | 200 |  | 400
|  | 33 | B11 | 20 | 4 | 4 | COPY RM / CHIEF ENGR / STORE FCU | [13 empty] | 3 |  |  |  | 200 |  |  | 600
|  | 34 | R12 | 20 | 4 | 4 | DIV MANAGER / SECRETARY FCU | [13 empty] | 2 |  |  |  | 200 | 400
|  | 35 | Y12 | 20 | 4 | 4 | SPA | [13 empty] | 5 |  |  |  | 200 |  | 1000
|  | 36 | B12 | 20 | 4 | 4 | SPA | [13 empty] | 1 |  |  |  | 200 |  |  | 200
[22 empty] | TOTAL CONNECTED LOAD |  |  |  | 9900 | 8050 | 6700 | 24650
[22 empty] | TOTAL CONNECTED LOAD (PF=0.8) |  |  |  | 12375 | 10062.5 | 8375 | 30812.5
[22 empty] | DIVERSITY FACTOR |  |  |  | 0.75
[22 empty] | TOTAL DIVERSITY LOAD |  |  |  | 23.1094 |  | KW
CABLE SIZE : | 4C 35 mm² Cu/XLPE/SWA/PVC + 1C 16 mm² Cu/PVC ECC
W/H:WATER HEATER , WM: WASHING MACHINE, FCU - FAN COIL UNIT, H/D- HAND DRYER

## 1-SPA2
Project : | JBH - TALISE GYM | [5 empty] | LOAD DISTRIBUTION SCHEDULE
DB No: DB-1-SPA2 | [6 empty] | (3-PHASE)
Fed from: SMDB/1
NOTE: NEW DB, TO REPLACE DB-1-K2 | [19 empty] | Location of DB : |  | 1ST FLOOR, TECH ROOM2
Rating of Incomer | Ratg of ELCB | SL. NO. | CIR. No. | MCB Rtg in (A) | CCT wire size mmsq | RCC wire size mmsq | Room / Area | [12 empty] | Watts Each | Load Per Phase - Watts |  |  | Remarks
[8 empty] | LTG | LTG | LTG | 13A | 13A | 15A | WH | HD | FCU | SPUR | ISOL | TOTAL
[8 empty] | 1 | 2 | 3 | SO | TSO | SO | [7 empty] | R | Y | B
[11 empty] | 200 | 400
160A TPN ISOLATOR | 40A 100mA 4P | 1 | R1 | 63 | 16 | 16 | DB - 1 - SPA3 | [13 empty] | 2476
|  | 2 | Y1 | [18 empty] | 2370
|  | 3 | B1 | [19 empty] | 3445
| 40A 30mA 4P | 4 | R2 | 20 | 4 | 4 | WC-SENSORY FLUSH | [9 empty] | 3 |  |  | 50 | 150
|  | 5 | Y2 | 20 | 4 | 4 | RELAXATION ROOM |  |  |  |  | 2 | [9 empty] | 800
|  | 6 | B2 | 20 | 4 | 4 | RELAXATION ROOM |  |  |  |  | 1 | [10 empty] | 400
| 40A 30mA 4P | 7 | R3 | 20 | 4 | 4 | COUPLE SAUNA | [10 empty] | 1 |  | 9000 | 3000
|  | 8 | Y3 | [18 empty] | 3000
|  | 9 | B3 | [19 empty] | 3000
| 40A 30mA 4P | 10 | R4 | 20 | 4 | 4 | COUPLE STEAM GENERATOR | [10 empty] | 1 |  | 4900 | 1633.3333
|  | 11 | Y4 | [18 empty] | 1633.3333
|  | 12 | B4 | [19 empty] | 1633.3333
| 40A 30mA 4P | 13 | R5 | 20 | 4 | 4 | MALE SAUNA | [10 empty] | 1 |  | 9000 | 3000
|  | 14 | Y5 | [18 empty] | 3000
|  | 15 | B5 | [19 empty] | 3000
| 40A 30mA 4P | 16 | R6 | 20 | 4 | 4 | FM. ICE FOUNTAIN | [10 empty] | 1 |  | 800 | 800
|  | 17 | Y6 | 20 | 4 | 4 | FM. HEATED BENCH | [10 empty] | 1 |  | 1220 |  | 1220
|  | 18 | B6 | 20 | 4 | 4 | M. HEATED BENCH | [10 empty] | 1 |  | 1220 |  |  | 1220
| 40A 30mA 4P | 19 | R7 | 20 | 4 | 4 | M. ICE FOUNTAIN | [10 empty] | 1 |  | 800 | 800
|  | 20 | Y7 | 20 | 4 | 4 | FEMALE EXPERIENCE SHOWER | [10 empty] | 1 |  | 100 |  | 100
|  | 21 | B7 | 20 | 4 | 4 | MALE EXPERIENCE SHOWER | [10 empty] | 1 |  | 100 |  |  | 100
| 40A 30mA 4P | 22 | R8 | 20 | 4 | 4 | COUPLE HAMMAM | [10 empty] | 1 |  | 1500 | 1500
|  | 23 | Y8 | [18 empty] | 0
|  | 24 | B8 | [19 empty] | 0
| 40A 30mA 4P | 25 | R9 | [17 empty] | 0
|  | 26 | Y9 | 40 | 10 | 10 | WHIRLPOOL | [12 empty] | 5750 |  | 5750
|  | 27 | B9 | [19 empty] | 0
| 40A 30mA 4P | 28 | R10 | 20 | 4 | 4 | TECH. ROOM 1 |  |  |  | 1 | 1 | [8 empty] | 600
|  | 29 | Y10 | 20 | 4 | 4 | TECH. ROOM 2 |  |  |  | 1 | [10 empty] | 200
|  | 30 | B10 | 20 | 4 | 4 | MALE EXPERIENCE SHOWER |  |  |  | 1 | [11 empty] | 200
| 40A 30mA 4P | 31 | R11 | 40 | 10 | 10 | FEMALE STEAM GENERATOR | [10 empty] | 1 |  | 12300 | 4100
|  | 32 | Y11 | [18 empty] | 4100
|  | 33 | B11 | [19 empty] | 4100
| 40A 30mA 4P | 34 | R12 | 40 | 10 | 10 | MALE STEAM GENERATOR | [10 empty] | 1 |  | 12300 | 4100
|  | 35 | Y12 | [18 empty] | 4100
|  | 36 | B12 | [19 empty] | 4100
[17 empty] | TOTAL CONNECTED LOAD |  |  |  | 22159.3333 | 26273.3333 | 21198.3333 | 69631
[17 empty] | TOTAL CONNECTED LOAD (PF=0.8) |  |  |  | 27699.1667 | 32841.6667 | 26497.9167 | 87038.75
[17 empty] | DIVERSITY FACTOR |  |  |  | 0.75
[17 empty] | TOTAL DIVERSITY LOAD |  |  |  | 65.2791 |  | KW
CABLE SIZE : | 4C 70 mm² Cu/XLPE/SWA/PVC + 1C 35 mm² Cu/PVC ECC
W/H:WATER HEATER , WM: WASHING MACHINE, FCU - FAN COIL UNIT, H/D- HAND DRYER

## 1-SPA-1
Project : | JBH - TALISE GYM | [5 empty] | LOAD DISTRIBUTION SCHEDULE
DB No: DB-1-SPA-1 | [6 empty] | (3-PHASE)
Fed from: SMDB/1
NOTE: | [20 empty] | Location of DB : |  | 1ST FLOOR, TECH ROOM2
Rating of Incomer | Ratg of ELCB | SL. NO. | CIR. No. | MCB Rtg in (A) | CCT wire size mmsq | RCC wire size mmsq | Room / Area | [13 empty] | Watts Each | Load Per Phase - Watts |  |  | Remarks
[8 empty] | LTG | LTG | LTG | 13A | 13A | 15A | SH | WH | HD | FCU | SPUR | ISOL | TOTAL
[8 empty] | 1 | 2 | 3 | SO | TSO | SO | [8 empty] | R | Y | B
[11 empty] | 200 | 400 |  | 100 |  | 1500
100A TPN ISOLATOR | 63A 30mA 4P | 1 | R1 | 63 | 16 | 16 | DB-SP-LL | [14 empty] | 8262
|  | 2 | Y1 | [19 empty] | 9125.5
|  | 3 | B1 | [20 empty] | 8155
|  | 4 | R2 | [18 empty] | 0
|  | 5 | Y2 | [19 empty] | 0
|  | 6 | B2 | [20 empty] | 0
| 40A 30mA 4P | 7 | R3 | 20 | 4 | 4 | FEMALE TREATMENT CORRIDOR |  |  |  | 3 | [10 empty] | 600
|  | 8 | Y3 | 20 | 4 | 4 | MALE CORRIDOR |  |  |  | 5 | [11 empty] | 1000
|  | 9 | B3 | 20 | 4 | 4 | MALE TREATMENT CORRIDOR |  |  |  | 3 | [12 empty] | 600
|  | 10 | R4 | 32 | 4 | 4 | COUPLES TREATMENT ROOM |  |  |  |  | 5 | [9 empty] | 2000 |  |  | Ring
|  | 11 | Y4 | 32 | 4 | 4 | MALE TREATMENT ROOM-4 |  |  |  |  | 4 | [10 empty] | 1600 |  | Ring
|  | 12 | B4 | 32 | 4 | 4 | MALE TREATMENT ROOM-3 |  |  |  |  | 4 | [11 empty] | 1600 | Ring
| 40A 30mA 4P | 13 | R5 | 32 | 4 | 4 | MALE TREATMENT ROOM-2 |  |  |  |  | 4 | [9 empty] | 1600 |  |  | Ring
|  | 14 | Y5 | 32 | 4 | 4 | MALE TREATMENT ROOM-1 |  |  |  |  | 4 | [10 empty] | 1600 |  | Ring
|  | 15 | B5 | 20 | 4 | 4 | MALE PREP. |  |  |  | 1 | 1 | [11 empty] | 600
|  | 16 | R6 | 20 | 4 | 4 | FEMALE CHANGING AREA | [6 empty] | 1 |  | 1 | [5 empty] | 1600
|  | 17 | Y6 | 20 | 4 | 4 | COUPLES CHANGING AREA | [6 empty] | 1 |  | 1 | [6 empty] | 1600
|  | 18 | B6 | 20 | 4 | 4 | MALE CHANGING AREA | [6 empty] | 1 |  | 1 | [7 empty] | 1600
| 40A 100mA 4P | 19 | R7 | 20 | 4 | 4 | CORRIDOR,FCU | [9 empty] | 1 |  |  |  | 862 | 862
|  | 20 | Y7 | 20 | 4 | 4 | CORRIDOR,FCU | [9 empty] | 1 |  |  |  | 862 |  | 862
|  | 21 | B7 | 20 | 4 | 4 | CORRIDOR,FCU | [9 empty] | 1 |  |  |  | 862 |  |  | 862
|  | 22 | R8 | 20 | 4 | 4 | CORRIDOR,FCU | [9 empty] | 1 |  |  |  | 862 | 862
|  | 23 | Y8
|  | 24 | B8
[18 empty] | TOTAL CONNECTED LOAD |  |  |  | 15786 | 15787.5 | 13417 | 44990.5
[18 empty] | TOTAL CONNECTED LOAD (PF=0.8) |  |  |  | 19732.5 | 19734.375 | 16771.25 | 56238.125
[18 empty] | DIVERSITY FACTOR |  |  |  | 0.7
[18 empty] | TOTAL DIVERSITY LOAD |  |  |  | 39.3667 |  | KW
CABLE SIZE : | 4C 35 mm² Cu/XLPE/SWA/PVC + 1C 16 mm² Cu/PVC ECC
W/H:WATER HEATER , WM: WASHING MACHINE, FCU - FAN COIL UNIT, H/D- HAND DRYER

## SP-LL
Project : | JBH - TALISE GYM | [5 empty] | LOAD DISTRIBUTION SCHEDULE
DB No: DB-SP-LL | [6 empty] | (3-PHASE)
Fed from: DB-1-SPA1
NOTE: | [29 empty] | Location of DB : |  | 1ST FLOOR, TECH ROOM2
Rating of Incomer | Ratg of ELCB | SL. NO. | CIR. No. | MCB Rtg in (A) | CCT wire size mmsq | RCC wire size mmsq | Room / Area | Connected Load / Points | [21 empty] | Watts Each | Load Per Phase - Watts |  |  | Remarks
[13 empty] | LTG | LTG | LTG | LTG | LTG | LTG | LTG | SPA LIGHTING |  |  |  |  | LTG | JB | SH | OTHERS | TOTAL
[13 empty] | 101 | 102 | 601 | 602 | 701 | 702 | 703 | CL | UB | SF | SL | STRIP | 704 |  | S/O |  |  |  | R | Y | B
[8 empty] | LTG | HO OD | EX. FAN | SH. S/O | 13A SSO | 15 | 15 | 20 | 50 | 50 | 50 | 50 | 20 | 15 | 100 | 20 | 15 | 20 | 200 | 50 | 50
63A TPN ISOLATOR | 40A 100mA 4P | 1 | R1 | 16 | 2.5 | 2.5 | FEMALE WET AREA, STEAM ROOM | [5 empty] | 7.5 | 13.4 |  |  | 3 |  |  | 2 | 3.3 | [9 empty] | 553
|  | 2 | Y1 | 10 | 2.5 | 2.5 | FEMALE CHANGING AREA | [5 empty] | 21.8 | 1.2 |  |  | 5 | 11 | [7 empty] | 3 |  | 4 |  |  |  | 1745
|  | 3 | B1 | 16 | 2.5 | 2.5 | FEMALE CORRIDOR | [5 empty] | 16 |  |  |  | 38 | 12 | [6 empty] | 2 | 2 | [6 empty] | 3180
|  | 4 | R2 | 10 | 2.5 | 2.5 | COUPLES TREATMENT ROOM | [5 empty] | 18.4 | 13.1 |  |  | 7 | [8 empty] | 1 |  |  |  |  | 1022.5
|  | 5 | Y2 | 10 | 2.5 | 2.5 | COUPLES CHANGING ROOM | [5 empty] | 13.7 | 2.6 |  |  | 4 | 2 | [7 empty] | 2 | [5 empty] | 944.5
|  | 6 | B2 | 10 | 2.5 | 2.5 | COUPLE HAMMAM, STEAM ROOM | [6 empty] | 16.7 | [5 empty] | 8 |  |  | 7 | [9 empty] | 550.5
| 40A 100mA 4P | 7 | R3 | 10 | 2.5 | 2.5 | SPA ENTRY CORRIDOR | [5 empty] | 17.1 |  |  |  | 6 | 3 | [5 empty] | 3.5 |  | 2 |  | 4 |  |  | 1359
|  | 8 | Y3 | 10 | 2.5 | 2.5 | CORRIDOR | [9 empty] | 16 | [14 empty] | 800
|  | 9 | B3 | 10 | 2.5 | 2.5 | MALE WET AREA, SAUNA, STEAM | [5 empty] | 5.4 | 12.6 |  |  | 5 |  |  | 4 | [12 empty] | 600
|  | 10 | R4 | 10 | 2.5 | 2.5 | MALE WC, STEAM ROOM | [5 empty] | 2.4 | 7.2 |  |  | 1 | 1 |  | 2 | [5 empty] | 1 |  | 2 |  |  | 484
|  | 11 | Y4 | 10 | 2.5 | 2.5 | MALE CHANGING AREA , SHO | [5 empty] | 18.7 |  |  |  | 4 | 11 | [7 empty] | 3 |  | 2 |  |  |  | 1630.5
|  | 12 | B4 | 10 | 2.5 | 2.5 | B.O.H LIFT LOBBY, CLEAN LINEN STORAGE, MALE CORRIDOR | [5 empty] | 10.8 |  |  | 1 | 6 | 3 | [6 empty] | 3 | [7 empty] | 722
| 40A 100mA 4P | 13 | R5 | 10 | 2.5 | 2.5 | MALE CORRIDOR | [9 empty] | 8 | [13 empty] | 400
|  | 14 | Y5 | 10 | 2.5 | 2.5 | MALE CORRIDOR | [9 empty] | 12 | [14 empty] | 600
|  | 15 | B5 | 10 | 2.5 | 2.5 | MALE CORRIDOR | [9 empty] | 14 | [15 empty] | 700
|  | 16 | R6 | 10 | 2.5 | 2.5 | MALE TREATMENT CORRIDOR | [5 empty] | 10.1 |  |  |  |  | 7 | [8 empty] | 4 |  |  |  | 701.5
|  | 17 | Y6 | 10 | 2.5 | 2.5 | MALE TREATMENT ROOM 4 | [5 empty] | 10.1 |  |  |  | 5 | [14 empty] | 401.5
|  | 18 | B6 | 10 | 2.5 | 2.5 | MALE TREATMENT ROOM 1&2 | [5 empty] | 24.1 |  |  |  | 9 | 5 | [14 empty] | 1061.5
| 40A 100mA 4P | 19 | R7 | 10 | 2.5 | 2.5 | MALE TREATMENT ROOM 3 | [5 empty] | 10.5 |  |  |  | 4 | 1 | [12 empty] | 407.5
|  | 20 | Y7 | 10 | 2.5 | 2.5 | MALE RELAXATION ROOM | [5 empty] | 11.2 |  |  |  | 4 | [14 empty] | 368
|  | 21 | B7 | 10 | 2.5 | 2.5 | TECH ROOM 1 | [14 empty] | 2 | [10 empty] | 200
|  | 22 | R8 | 10 | 2.5 | 2.5 | TECH ROOM 2 | [14 empty] | 2 | [8 empty] | 200
|  | 23 | Y8 | 10 | 2.5 | 2.5 | FEMALE TREATMENT 1&2 , SHOWER | [5 empty] | 30 | 1.2 |  |  | 10 | 6 | [13 empty] | 1268
|  | 24 | B8 | 10 | 2.5 | 2.5 | FEMALE TREATMENT 3&4 | [5 empty] | 25.4 |  |  |  | 10 | 2 | [14 empty] | 981
| 40A 100mA 4P | 25 | R9 | 10 | 2.5 | 2.5 | FEMALE TREATMENT 5 | [5 empty] | 12.3 |  |  |  | 6 | 1 | [12 empty] | 534.5
|  | 26 | Y9 | 10 | 2.5 | 2.5 | FEMALE RELAXATION ROOM | [5 empty] | 11.2 |  |  |  | 4 | [14 empty] | 368
|  | 27 | B9 | 10 | 2.5 | 2.5 | FEMALE PREP | [17 empty] | 4 | [7 empty] | 80
|  | 28 | R10 | 10 | 2.5 | 2.5 | CORRIDOR | [18 empty] | 13 |  |  |  |  | 2600
|  | 29 | Y10 | 10 | 2.5 | 2.5 | FEMALE TREATMENT CORRIDOR | [18 empty] | 5 | [5 empty] | 1000
|  | 30 | B10 | 10 | 2.5 | 2.5 | MALE PREP | [18 empty] | 2 |  |  |  | 40 |  |  | 80
[26 empty] | TOTAL CONNECTED LOAD |  |  |  |  | 8262 | 9125.5 | 8155 | 25542.5
[26 empty] | TOTAL CONNECTED LOAD (PF=0.8) |  |  |  |  | 10327.5 | 11406.875 | 10193.75 | 31928.125
[26 empty] | DIVERSITY FACTOR |  |  |  |  | 0.9
[26 empty] | TOTAL DIVERSITY LOAD |  |  |  |  | 28.7353 |  | KW
CABLE SIZE : | 4C 16+ mm² Cu/XLPE/SWA/PVC + 1C 16 mm² Cu/PVC ECC
W/H:WATER HEATER , WM: WASHING MACHINE, FCU - FAN COIL UNIT, H/D- HAND DRYER

## 1-SPA-3
Project : | JBH - TALISE GYM | [5 empty] | LOAD DISTRIBUTION SCHEDULE
DB No: DB-1-SPA-3 | [6 empty] | (3-PHASE)
Fed from: DB-1-SPA2
NOTE: | [20 empty] | Location of DB : |  | 1ST FLOOR, RETAIL STORAGE
Rating of Incomer | Ratg of ELCB | SL. NO. | CIR. No. | MCB Rtg in (A) | CCT wire size mmsq | RCC wire size mmsq | Room / Area | [13 empty] | Watts Each | Load Per Phase - Watts |  |  | Remarks
[8 empty] | LTG | LTG | LTG | LTG | 13A | 13A | 15A | WH | HD | FCU | SPUR | ISOL | TOTAL
[8 empty] | 1 | 2 | 3 | 705 | SO | TSO | SO | [7 empty] | R | Y | B
[11 empty] | 42 | 200 | 400
40A TPN ISOLATOR | 40A 100mA 4P | 1 | R1 | 10 | 2.5 | 2.5 | RECEPTION (LGT-603,703) | 1 | 18 | [11 empty] | 50 | 950
|  | 2 | Y1 | 10 | 2.5 | 2.5 | RETAIL AND TESTING (LGT-703,601,101) | 9 | 1 | 10 | [10 empty] | 50,20,10 |  | 570
|  | 3 | B1 | 10 | 2.5 | 2.5 | DISPLAY & WAITING (LGT-101,703) | 16 | 22 | [11 empty] | 15,50 |  |  | 1340
|  | 4 | R2 | 10 | 2.5 | 2.5 | BY KITCHEN SPECIALIST |  |  |  | 3 | [10 empty] | 126
|  | 5 | Y2 | 10 | 2.5 | 2.5 | RETAIL (LGT-704 |  | 2 | [11 empty] | 20 |  | 200
|  | 6 | B2 | 10 | 2.5 | 2.5 | OUTDOOR BAR | 7 | [12 empty] | 15 |  |  | 105
| 40A 30mA 4P | 7 | R3 | 20 | 4 | 4 | RECEPTIOIN |  |  |  |  | 1 | 2 | [8 empty] | 1000
|  | 8 | Y3 | 20 | 4 | 4 | RECEPTION |  |  |  |  | 1 | 2 | [9 empty] | 1000
|  | 9 | B3 | 32 | 4 | 4 | WAITING AND CONSULTATION AREA | [5 empty] | 4 | [10 empty] | 1600 | Ring
|  | 10 | R4 | 20 | 4 | 4 | WAITING AND CONSULTATION AREA |  |  |  |  | 2 | [9 empty] | 400
|  | 11 | Y4 | 20 | 4 | 4 | BY KITCHEN SPECIALIST |  |  |  |  | 1 | 1 | [9 empty] | 600
|  | 12 | B4 | [20 empty] | 0
| 40A 30mA 4P | 13 | R5 | [18 empty] | 0
|  | 14 | Y5 | [19 empty] | 0
|  | 15 | B5 | 20 | 4 | 4 | OUTDOOR BAR | [5 empty] | 1 | [10 empty] | 400
|  | 16 | R6 | [18 empty] | 0
|  | 17 | Y6 | [19 empty] | 0
|  | 18 | B6 | [20 empty] | 0
| 40A 30mA 4P | 19 | R7 | [18 empty] | 0
|  | 20 | Y7 | [19 empty] | 0
|  | 21 | B7 | [20 empty] | 0
|  | 22 | R8 | [18 empty] | 0
|  | 23 | Y8 | [19 empty] | 0
|  | 24 | B8 | [20 empty] | 0
[18 empty] | TOTAL CONNECTED LOAD |  |  |  | 2476 | 2370 | 3445 | 8291
[18 empty] | TOTAL CONNECTED LOAD (PF=0.8) |  |  |  | 3095 | 2962.5 | 4306.25 | 10363.75
[18 empty] | DIVERSITY FACTOR |  |  |  | 0.7
[18 empty] | TOTAL DIVERSITY LOAD |  |  |  | 7.2546 |  | KW
CABLE SIZE : | 4C 10 mm² Cu/XLPE/SWA/PVC + 1C 10 mm² Cu/PVC ECC
W/H:WATER HEATER , WM: WASHING MACHINE, FCU - FAN COIL UNIT, H/D- HAND DRYER