## SMDB-1
BOND FURNITURE INDUSTRIES L.L.C.
P.O.BOX 15758
DUBAI, UNITED ARAB EMIRATES
TEL : 971-4-2711727
FAX : 971-4-2713797
ELECTRICAL DISTRIBUTION BOARD
PANEL LOCATION: |  |  | COMMISSIONING RECORD SHEET: | [6 empty] | PANEL REF: | [7 empty] | SHEET:
PANEL DETAILS: |  |  | PROJECT:
PROTECTIVE DEVISE TYPE: |  |  | SOURCE: | [6 empty] | CPC: | [7 empty] | TEST VOLTAGE:
|  |  | RATING: | [6 empty] | SETTING:
SUPPLY CABLE SIZE:
CIRCUIT DETAILS: | [8 empty] | COLD TEST
CIRCUIT REF. | CIRCUIT DESIGNATION | CABLE (mm2) | ECC (mm2) | NO OF Cores | MCCB Amp | MCB Type | MCB (KA) | RCCB (mA) | INSULATION RESISTANCE | [5 empty] | Continuity Test | Ring | Resistance (R1+R2) OHM | REMARKS
[9 empty] | R-Y | Y-B | B-R | RYB-N | RYB-E | N-E
1 | DB-1-N2 | 35 | 16 | 4 | 63 |  | 32 |  | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | OK | N/A | 0.2
2 | DB-1-N4 | 25 | 16 | 4 | 63 |  | 32 |  | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | OK | N/A | 0.8
3 | DB-1-N1 | 25 | 16 | 2 | 63 |  | 32 |  | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | OK | N/A | 0.6
4 | DB-1-27.00 | 25 | 16 | 4 | 63 |  | 32 |  | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | OK | N/A | 1
5 | DB-1-K1 | 70 | 35 | 4 | 100 |  | 32 |  | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | OK | N/A | 1.4
6 | DB-1-23 | 25 | 16 | 4 | 63 |  | 32 |  | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | OK | N/A | 0.3
7 | DB-1-39.00 | 25 | 16 | 2 | 63 |  | 32 |  | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | OK | N/A | 1.5
8 | DB-1-40.00 | 25 | 16 | 2 | 63 |  | 32 |  | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | OK | N/A | 0.7
9 | DB-1-41.00 | 25 | 16 | 2 | 63 |  | 32 |  | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | OK | N/A | 0.7
10 | SMDB-DB-1-N3 | 240 | 120 | 4 | 250 |  | 32 |  | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | OK | N/A | 0.2
11 | DB-1-32.00 | 25 | 16 | 2 | 63 |  | 32 |  | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | OK | N/A | 0.3
12 | DB-1-35.00 | 25 | 16 | 2 | 63 |  | 32 |  | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | OK | N/A | 0.5
13 | DB-1-38.00 | 25 | 16 | 2 | 63 |  | 32 |  | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | OK | N/A | 0.5
14 | DB-1-36.00 | 25 | 16 | 2 | 63 |  | 32 |  | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | OK | N/A | 1
15 | DB-1-37.00 | 25 | 16 | 2 | 63 |  | 32 |  | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | OK | N/A | 0.5
16 | DB-1-35.01 | 25 | 16 | 2 | 63 |  | 32 |  | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | OK | N/A | 0.7
17 | DB-1-RL | 25 | 16 | 4 | 63 |  | 32 |  | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | OK | N/A | 0.8
18 | SPARE |  |  |  | 63 |  | 32
19 | DB-1-25.00 | 25 | 16 | 2 | 63 |  | 32 |  | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | OK | N/A | 0.7
20 | DB-1-24.02 | 25 | 16 | 2 | 63 |  | 32 |  | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | OK | N/A | 1.4
21 | CB-1-N4 | 10 | 10 | 2 | 25 |  | 32 |  | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | OK | N/A | 1.4
22 | SPARE
23 | SPARE
24 | SPARE
25 | DB-1-SPA-1 | 35 | 16 | 4 | 100 |  | 32 |  | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | OK | N/A | 1.3
26 | CB-1-N1 | 6 | 6 | 2 | 25 |  | 32 |  | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | OK | N/A | 1.3
27 | CB-1-N2 | 10 | 10 | 2 | 25 |  | 32 |  | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | OK | N/A | 0.3
28 | CB-1-N3 | 10 | 10 | 2 | 25 |  | 32 |  | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | OK | N/A | 0.4
29 | DB-1-SPA-2 | 70 | 35 | 4 | 160 |  | 32 |  | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | OK | N/A | 1.2
30 | DB-1-N5 | 25 | 16 | 4 | 63 |  | 32 |  | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | OK | N/A | 0.1
NOTES: TEST READING ARE WITHIN THE LIMIT |  |  |  |  | COLD TESTED BY:
WITNESSED BY:
ACCEPTED BY: |  |  |  |  | TEST INSTRUMENT: | [5 empty] | SERIAL NUMBER: |  |  |  |  | CALIBRATION DATE:

## DB-1-N2
BOND FURNITURE INDUSTRIES L.L.C.
P.O.BOX 15758
DUBAI, UNITED ARAB EMIRATES
TEL : 971-4-2711727
FAX : 971-4-2713797
ELECTRICAL DISTRIBUTION BOARD
PANEL LOCATION: |  |  | COMMISSIONING RECORD SHEET: | [6 empty] | PANEL REF: | [11 empty] | SHEET:
PANEL DETAILS: |  |  | PROJECT: | [13 empty] | PANEL IR TEST
PROTECTIVE DEVISE TYPE: |  |  | SOURCE: | [6 empty] | CPC: | [6 empty] | R-Y | Y-B | B-R | RYB-N | RYB-E | TEST VOLTAGE:
|  |  | RATING: | [6 empty] | SETTING: | [6 empty] | >2000 | >2000 | >2000 | >2000 | >2000
SUPPLY CABLE SIZE:
CIRCUIT DETAILS: | [8 empty] | COLD TEST
CIRCUIT REF. | CIRCUIT DESIGNATION | CABLE (mm2) | ECC (mm2) | NO OF Cores | MCCB Amp | MCB Type | MCB (KA) | ELCB Rating | INSULATION RESISTANCE | [9 empty] | Continuity Test | Ring | Resistance (R1+R2) OHM | REMARKS
[9 empty] | R-Y | Y-B | B-R | R-N | Y-N | B-N | R-E | Y-E | B-E | N-E
R1 | F&B / DIV MANAGER OFFICE LIGHTING | 2.5 | 2.5 |  | 10 |  |  | 63A 100mA 4P | N/A | N/A | N/A | >2000 |  |  | >2000 |  |  | >2000 | OK | N/A | 0.9
Y1 | SECRETARY AREA LIGHTING | 2.5 | 2.5 |  | 10 |  |  |  | N/A | N/A | N/A |  | >2000 |  |  | >2000 |  | >2000 | OK | N/A | 1.2
B1 | COPY RM/CHIEF ENGR/STORE LIGHTING | 2.5 | 2.5 |  | 10 |  |  |  | N/A | N/A | N/A |  |  | >2000 |  |  | >2000 | >2000 | OK | N/A | 0.2
R2 | DIR OF PERSONNEL OFFICE LIGHTING | 2.5 | 2.5 |  | 10 |  |  |  | N/A | N/A | N/A | >2000 |  |  | >2000 |  |  | >2000 | OK | N/A | 0.9
Y2 | SPARE |  |  |  | 10
B2 | SPARE |  |  |  | 10
R3 | SPARE |  |  |  | 10 |  |  | 63A 100mA 4P
Y3 | SPARE |  |  |  | 10
B3 | SPARE |  |  |  | 10
R4 | SPARE |  |  |  | 10
Y4 | LINEN ROOM LIGHTING | 2.5 | 2.5 |  | 10 |  |  |  | N/A | N/A | N/A |  | >2000 |  |  | >2000 |  | >2000 | OK | N/A | 1
B4 | SPARE |  |  |  | 10
R5 | FEMALE RELAXATION ROOM | 4 | 4 |  | 20 |  |  | 63A 30mA 4P | N/A | N/A | N/A | >2000 |  |  | >2000 |  |  | >2000 | OK | N/A | 0.2
Y5 | SPARE |  |  |  | 10
B5 | SPARE |  |  |  | 10
R6 | SPARE |  |  |  | 10
Y6 | SPARE |  |  |  | 10
B6 | SPARE |  |  |  | 10
R7 | F&B / DIV MNAGER 13A RING | 4 | 4 |  | 32 |  |  | 63A 30mA 4P | N/A | N/A | N/A | >2000 |  |  | >2000 |  |  | >2000 | OK | N/A | 0.6
Y7 | SECRETARY AREA 13A RING | 4 | 4 |  | 32 |  |  |  | N/A | N/A | N/A |  | >2000 |  |  | >2000 |  | >2000 | OK | N/A | 0.8
B7 | COPY RM/CHIEF ENGR/STORE 13A RING | 4 | 4 |  | 32 |  |  |  | N/A | N/A | N/A |  |  | >2000 |  |  | >2000 | >2000 | OK | N/A | 0.5
R8 | DIR OF PERSONNEL OFICE 13A RING | 4 | 4 |  | 32 |  |  |  | N/A | N/A | N/A | >2000 |  |  | >2000 |  |  | >2000 | OK | N/A | 0.3
Y8 | SPARE |  |  |  | 32
B8 | SPARE |  |  |  | 32
R9 | FEMALE TREATMENT ROOM 1 | 4 | 4 |  | 32 |  |  | 63A 30mA 4P | N/A | N/A | N/A | >2000 |  |  | >2000 |  |  | >2000 | OK | N/A | 0.7
Y9 | FEMALE TREATMENT ROOM 2 | 4 | 4 |  | 32 |  |  |  | N/A | N/A | N/A |  | >2000 |  |  | >2000 |  | >2000 | OK | N/A | 1
B9 | FEMALE TREATMENT ROOM 3 | 4 | 4 |  | 32 |  |  |  | N/A | N/A | N/A |  |  | >2000 |  |  | >2000 | >2000 | OK | N/A | 1.1
R10 | FEMALE TREATMENT ROOM 4 | 4 | 4 |  | 32 |  |  |  | N/A | N/A | N/A | >2000 |  |  | >2000 |  |  | >2000 | OK | N/A | 1.1
Y10 | FEMALE TREATMENT ROOM 5 | 4 | 4 |  | 32 |  |  |  | N/A | N/A | N/A |  | >2000 |  |  | >2000 |  | >2000 | OK | N/A | 0.8
B10 | FEMALE PREP | 4 | 4 |  | 32 |  |  |  | N/A | N/A | N/A |  |  | >2000 |  |  | >2000 | >2000 | OK | N/A | 0.8
R11 | F@B/DIV MANAGER/DIR PER FCU | 4 | 4 |  | 20 |  |  | 63A 100mA 4P | N/A | N/A | N/A | >2000 |  |  | >2000 |  |  | >2000 | OK | N/A | 0.9
Y11 | SECRETARY AREA FCU | 4 | 4 |  | 20 |  |  |  | N/A | N/A | N/A |  | >2000 |  |  | >2000 |  | >2000 | OK | N/A | 0.6
B11 | COPY RM / CHIEF ENGR / STORE FCU | 4 | 4 |  | 20 |  |  |  | N/A | N/A | N/A |  |  | >2000 |  |  | >2000 | >2000 | OK | N/A | 0.8
R12 | DIV MANAGER / SECRETARY FCU | 4 | 4 |  | 20 |  |  |  | N/A | N/A | N/A | >2000 |  |  | >2000 |  |  | >2000 | OK | N/A | 0.3
Y12 | SPA | 4 | 4 |  | 20 |  |  |  | N/A | N/A | N/A |  | >2000 |  |  | >2000 |  | >2000 | OK | N/A | 0.3
B12 | SPA | 4 | 4 |  | 20 |  |  |  | N/A | N/A | N/A |  |  | >2000 |  |  | >2000 | >2000 | OK | N/A | 1.3
NOTES: TEST READING ARE WITHIN THE LIMIT |  |  |  |  | COLD TESTED BY: | [14 empty] | DATE:
[5 empty] | WITNESSED BY: | [14 empty] | DATE:
ACCEPTED BY: |  |  |  |  | TEST INSTRUMENT: |  |  |  | INSULATION RESISTANCE B-R: SERIAL NUMBER:
[9 empty] | INSULATION RESISTANCE B-R: CALIBRATION DATE: |  | DATE: